## Slide 1
PLC4X Manager
Technical Architecture & Implementation Guide
For IT Infrastructure & Industrial Automation Teams
Technical Presentation | 2026

## Slide 2
System Architecture
6 Docker containers, fully orchestrated with docker-compose
Container | Ports | Description
plc4x-admin | 3080, 3443 | FastAPI + uvicorn, Web UI, HMI editor, WebSocket, MQTT/InfluxDB writer, SQLite DB
plc4x-server | 12687 | Apache PLC4X OPC-UA Server (Java) + pylogix service (Python, port 5000)
influxdb | 8086 | Time-series DB: 90-day raw, 2-year hourly, daily forever
grafana | 3000 | 8 dashboards, 5 alert rules, InfluxDB + MQTT datasources
mosquitto | 1883 | MQTT broker for real-time tag streaming
plc4x-ml | - | 7 ML algorithms: Prophet, IForest, PyOD, SHAP, ruptures, stumpy, correlation

## Slide 3
Data Flow Pipeline
1. PLC4X Server connects to PLCs via S7/Modbus/OPC-UA/EIP protocols
2. PLC4X Server exposes all tags via OPC-UA (port 12687)
3. pylogix service (port 5000) provides direct Rockwell tag discovery & diagnostics
4. Background Poller (Python asyncua) reads OPC-UA every 5s (configurable per device)
5. Poller writes to: JSON cache (instant API), InfluxDB (SYNCHRONOUS), MQTT (real-time)
6. Virtual tags bypass OPC-UA — stored in JSON file, written via REST API
7. Calculated tags evaluated after each poll: formulas on other tag values
8. Alarm engine evaluates thresholds every cycle, persists to SQLite alarm_history table
9. WebSocket pushes live data, alarm events, and MQTT messages to browser clients
10. ML container queries InfluxDB every 5min: 7 algorithms run on all active tags
11. Grafana queries InfluxDB directly for dashboards and alerts
12. Web UI reads from JSON cache (~60ms) instead of direct OPC-UA (~1s)

## Slide 4
Supported PLC Protocols
Protocol | Connection String | Tag Example
Siemens S7 | s7://192.168.1.10 | %DB1:0:REAL
Modbus TCP | modbus-tcp://192.168.1.20:502 | holding-register:1
Modbus RTU/ASCII | modbus-rtu:///dev/ttyUSB0 | holding-register:1
OPC-UA Client | opcua:tcp://192.168.1.30:4840 | ns=2;i=10
Allen-Bradley Logix | logix://192.168.1.50 | MyTag
EtherNet/IP | eip://192.168.1.40 | %MyTag:DINT
KNXnet/IP | knxnet-ip://192.168.1.60 | 1/1/1:DPT_Switch
IEC 60870-5-104 | iec-60870-5-104://192.168.1.70 | M_ME_NC_1:5:20
Firmata (Arduino) | firmata:///dev/ttyACM0 | digital:13
Simulated (Test) | simulated://127.0.0.1 | RANDOM/Temporary:DINT

## Slide 5
Rockwell Allen-Bradley Integration (pylogix)
Direct EtherNet/IP CIP communication — no RSLinx or middleware required
Discovery Endpoints:
POST /api/plctag/discover
- Controller + program tags
- Tag name, type, array, UDT info
POST /api/plctag/discover/programs
- List all program names
Diagnostics Endpoints:
POST /api/plctag/diagnostics/identity
- Vendor, model, firmware, serial
POST /api/plctag/diagnostics/health
- Identity + tag count + programs
Safety Rules (plctag_safety.py):
R1: Global lock - ONE CIP connection
R2: Short-lived - 10s max per operation
R3: Socket timeout - 3-5s (no hung TCP)
R5: Rate limit - 30s cooldown per PLC IP
R7: Connection counting & logging
R8: No retry - fail-fast on error
R10: Admin-only access
Supported PLC Types:
- CompactLogix (1769-L series)
- ControlLogix (1756-L series)
- Communication via 1768-ENBT/A

## Slide 6
Security Architecture
Authentication:
- JWT HS256 tokens (configurable expiry)
- Brute-force: 5 fails = 5-min IP lockout
- API key for machine-to-machine access
Authorization (RBAC):
- 3 roles: admin / operator / monitor
- Plant-based access filter (USERS_JSON)
- Per-device allowWrite flag
PLC Write Protection (4 layers):
- PLC_READONLY=true (global, default ON)
- Device allowWrite=false (per device)
- Role 'monitor' (no PLC writes)
- Plant filter (restrict by plant)
Transport:
- HTTPS auto-generated TLS (port 3443)
- OPC-UA Basic256Sha256 + SignAndEncrypt
- Certificate-based auth (PKI trust store)
Data Protection:
- SQLite audit trail (user, IP, timestamp)
- Flux injection regex allowlist
- XSS protection (escHtml/escAttr)
- HMAC constant-time comparison
- FileLock cross-process file access
PLC Safety:
- Global CIP connection lock
- Rate limiting per PLC IP (30s)
- Socket timeout (prevents hung connections)

## Slide 7
Alarm System - Deep Dive
Per-tag thresholds:
- warningHigh / warningLow
- criticalHigh / criticalLow
- Validation: CL <= WL <= WH <= CH
Conditional profiles:
- Condition tag (e.g., ProductCode)
- Multiple profiles per product
- Fallback to default thresholds
Sound notification:
- 880Hz beep for critical unack
- 30s cooldown between beeps
- AudioContext with resume()
Evaluation engine:
- Runs every poller cycle
- Persisted to SQLite alarm_history
- Active alarms in .alarms.json
State management:
- Active alarms with acknowledge
- History (SQLite, unlimited)
- Severity escalation tracking
- Orphan cleanup on config change
Integration:
- WebSocket: real-time alarm push
- MQTT: plc4x/_alarms/{device}/{tag}
- Grafana: 5 pre-configured alert rules
- HMI: alarm banner element (blinks)

## Slide 8
HMI / Synoptic System
Konva.js 9.x canvas with 16 element types
Hierarchy: Plant > Area > Equipment > Screen
Full CRUD + rename for all levels
Drag-and-drop element placement
Property panel with tag selection
Per-element device override
Background image upload
Zoom/pan with mouse wheel
Fullscreen mode (?hmi=equip-id)
Auto-save on every change
Demo with 21 elements pre-configured
16 Element Types:
Display, Gauge, Tank, Bar Graph,
Progress Bar, Indicator, Valve, Motor,
Pipe (animated flow), Alarm Banner,
Label, Image, Button, Switch,
Slider, Numeric Input
Write Controls (with confirmation):
- Button: write value on click
- Switch: toggle ON/OFF
- Valve: open/close
- Motor: start/stop
- Slider: drag to set value
- Numeric Input: type value

## Slide 9
Virtual & Calculated Tags
Virtual Tags (address: VIRTUAL):
- No PLC connection needed
- Value set via REST API or HMI
- Stored in .virtual-tags.json
- Cross-process safe (FileLock)
- Flows to: MQTT, InfluxDB, Grafana
- Use cases:
- Product code selection
- Manual quality inputs
- Shift/batch identifiers
- External system integration
Calculated Tags (formula-based):
- Safe expression evaluator (AST)
- Supports: +, -, *, /, **, %
- Functions: abs, min, max, sqrt, round
- Comparisons: >, <, ==, if/else
- Can chain (tag B uses tag A)
- Use cases:
- Efficiency = output / input * 100
- Delta = current - previous
- Weighted average
- Boolean logic combinations

## Slide 10
OEE (Overall Equipment Effectiveness)
OEE = Availability x Performance x Quality
Configuration per device:
- Running Tag: boolean/status tag indicating machine is ON
- Production Count Tag: cumulative counter (handles rollover)
- Reject Count Tag: cumulative reject counter (optional)
- Ideal Cycle Time: seconds per unit at max speed
- Planned Hours/Day: scheduled production hours
Calculation from InfluxDB history:
- Availability = (running intervals sum) / planned time
- Performance = (ideal cycle time x total count) / run time
- Quality = (total count - rejects) / total count
SVG gauges: green >= 85%, yellow 60-85%, red < 60%
Trend chart: availability over time (hourly/daily buckets)
Inline OEE on multi-plant dashboard for each configured device

## Slide 11
REST API Overview (50+ endpoints)
Authentication:
POST /api/auth/login
GET /api/auth/verify
Devices & Tags:
CRUD /api/devices, /api/devices/:name/tags
PUT /api/devices/:name/tags/:alias/alarms
PUT /api/devices/:name/oee-config
Live Data:
GET /api/live/read
POST /api/live/write
HMI:
CRUD /api/hmi/plants, areas, equipment
PUT /api/hmi/equipment/:id/screen
Rockwell/pylogix:
POST /api/plctag/discover
POST /api/plctag/diagnostics/identity
POST /api/plctag/diagnostics/health
Alarms & OEE:
GET /api/alarms
POST /api/alarms/acknowledge
GET /api/oee/calculate, /api/oee/trend
Reports & Audit:
GET /api/export/csv, /api/export/pdf
GET/POST /api/logbook
GET /api/audit
WebSocket: ws://.../ws/live

## Slide 12
Deployment & Infrastructure
Requirements:
- Docker + Docker Compose
- 8GB RAM (16GB with ML analytics)
- Linux, Windows, or macOS
- Network access to PLCs
Installation (3 commands):
git clone <repo>
cp .env.example .env
docker compose up -d
Cloud Deployment (Coolify):
- GitHub auto-deploy on push
- No bind mounts (all Dockerfiles)
- Ports: 3080/3443 (no Traefik conflict)
- Named volumes for persistence
Persistence (Docker volumes):
- config-data: YAML, SQLite, backups
- security-data: certs, keystore, PKI
- influxdb-data: time-series history
- grafana-data: dashboard customizations
- mosquitto-data: MQTT persistence
Monitoring room:
- Kiosk mode: ?kiosk URL parameter
- Auto-cycles: Dashboard, HMI, OEE
- 20 kiosks, 60 clients supported
- Fullscreen browser on TV
Networking:
- Bridge mode (default) or host mode
- HTTPS on port 3443 (self-signed)

## Slide 13
Grafana Dashboards & ML Analytics
8 Pre-configured Dashboards:
1. Overview - all devices at a glance
2. Plant Overview - filtered by plant
3. Device Detail - deep dive per device
4. Energy Dashboard - power metrics
5. AI Predictions - Prophet forecasts
6. Alarms & Anomalies - ML alerts
7. Custom Data - external sources
8. System Health - latency, errors
5 Alert Rules:
- Device Offline (1m threshold)
- High Read Latency (>2000ms)
- ML Anomaly Detected
- No Data from Poller (2m)
- High Tag Error Rate (>10)
7 ML Algorithms (plc4x-ml container):
1. Prophet - 2h forecast + confidence
2. Isolation Forest - anomaly scoring
3. PyOD Ensemble - ECOD+LOF+IForest
4. SHAP - explainable anomaly causes
5. ruptures - change point detection
6. stumpy - pattern matching (motifs)
7. numpy - cross-tag correlation
Configuration (per device in config.yml):
- Enable/disable each algorithm
- Contamination, min agreement
- Segment size, penalty, window size
- Manual 'Run Now' button in UI

## Slide 14
Data Retention & Storage
Storage | Content | Frequency | Retention
plc4x_raw | Raw tag values | Every poll cycle (5s default) | 90 days
plc4x_hourly | Hourly aggregates | Mean, min, max per hour | 2 years
plc4x_daily | Daily aggregates | Mean, min, max per day | Forever
plc4x_health | Device health | Status, latency, tag counts | 90 days
plc4x_forecast | ML predictions | Prophet forecasts | 30 days
plc4x_anomaly | Anomaly scores | All 7 ML algorithm results | 30 days
SQLite: audit_entries | Audit trail | All write operations (user, IP) | Unlimited
SQLite: alarm_history | Alarm events | Fire, ack, clear with duration | Unlimited
SQLite: logbook_entries | Shift logbook | Operator observations | Unlimited
SQLite: write_log | PLC writes | Tag, value, user, timestamp | Unlimited